## Low Cost
Principal Inputs |  |  | Fixed/Computed Variables
Biogas capture rate (MMBtu/y) | 1000000 |  | MMBtu/y -> SCFH | 0.2021
Project lifetime (y) | 30 |  | Gas loss associated w/ lt. conditioning | 0.03
Discount rate | 7% |  | Project cumulative discount factor (PCDF) | 12.409
PCDF = the sum of the present value factors for each of a series of periods at a given discount rate
Data for light biogas conditioning - water removal only
Conditioner ID | Biogas Conditioning Unit | Unit Cost ($/unit) | Operation & Maintenance Cost ($/year) | Operating Feed Flow (SCFH) | Product Output Flow (SCFH) | Technology Used for Conditioning
1 | Unison | 192000 | 13500 | 1500 | 1450 | Glycol chiller
2 | Unison | 266000 | 13500 | 4200 | 4100 | Glycol chiller
3 | Unison | 550000 | 16500 | 9000 | 8800 | Glycol chiller
4 | Unison | 810000 | 25000 | 12000 | 11500 | Glycol chiller
Data for microturbine electricity generators
Generator ID | Generator Model | Fuel Type (Biogas/ Natural Gas) | Power Generation Capacity (kWh) | Fuel Consumption Rate (SCFH) | Generator Cost ($/ unit) | Operation & Maintenance Cost ($/year)
1 | Capstone | Biogas | 65 | 1500 | 106500 | 10000
2 | Capstone | Biogas | 200 | 4000 | 325000 | 25500
3 | GE | Biogas | 320 | 7020 | 1575000 | 78840
4 | GE | Biogas | 613 | 12600 | 1990000 | 131400
5 | GE | Biogas | 823 | 16800 | 2150000 | 157680
6 | GE | Biogas | 1029 | 20580 | 2335000 | 175200
Optimization | DECISION VARIABLES | Parameters |  |  |  |  | Constraints (SCFH)
Conditioner ID | Number of Units | Capital Cost | O&M Cost | Summed Cost | Gas Conditioning Cap. | Total Conditioning Capacity | 202400 | ≥ | 202100 | Total Conditionable Biogas
1 | 0 | 0 | 0 | 0 | 0 | Total Generator Gas Consumption Capacity | 196500 | ≥ | 196037 | Total Conditioned Biogas
2 | 0 | 0 | 0 | 0 | 0 | Decision Variables |  | = | Integers
3 | 23 | 12650000 | 4709231.1291 | 17359231.1291 | 202400 | Total Conditioning Cost
4 | 0 | 0 | 0 | 0 | 0 | 17359231.1291
Generator ID | Number of Units | Capital Cost | O&M Cost | Summed Cost | Gas Consumption Cap.
1 | 131 | 13951500 | 16255843.9504 | 30207343.9504 | 196500
2 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | Total Generator Cost
6 | 0 | 0 | 0 | 0 | 0 | 30207343.9504
MINIMIZATION
TOTAL PROJECT COST
47566575.0795

## High Cost
Principal Inputs |  |  | Fixed/Computed Variables
Biogas capture rate (MMBtu/y) | 89000 |  | MMBtu/y -> SCFH | 0.2021
Project lifetime (y) | 30 |  | Gas loss associated w/ hvy. conditioning | 0.43
Discount rate | 7% |  | Project cumulative discount factor (PCDF) | 12.409
PCDF = the sum of the present value factors for each of a series of periods at a given discount rate
Data for light biogas conditioning - water removal only
Conditioner ID | Biogas Conditionin g Unit | Unit Cost ($/unit) | Operation & Maintenanc e Cost ($/year) | Operating Feed Flow (SCFH) | Product Output Flow (SCFH) | Technology Used for Conditioning
1 | Guild | 422500 | 36535 | 6000 | 3240 | PSA
2 | Guild | 1385000 | 86600 | 21000 | 11880 | PSA
3 | Guild | 1500000 | 132000 | 42000 | 23700 | PSA
4 | Guild | 1900000 | 315100 | 72000 | 40680 | PSA
5 | Guild | 2600000 | 526200 | 120000 | 67740 | PSA
6 | Guild | 4300000 | 1276000 | 300000 | 169380 | PSA
Data for microturbine electricity generators
Generator ID | Generator model | Fuel Type (Biogas/ Natural Gas) | Power Generation Capacity (kWh) | Fuel Consumption Rate (SCFH) | Generator Cost ($/ unit) | Operation & Maintenance Cost ($/ year)
1 | Caterpillar | Natural Gas | 60 | 1650 | 85000 | 15000
2 | Caterpillar | Natural Gas | 150 | 1840 | 155000 | 25000
3 | GE | Natural Gas | 320 | 3420 | 1325000 | 73584
4 | Caterpillar | Natural Gas | 600 | 4860 | 850000 | 100000
5 | GE | Natural Gas | 613 | 6300 | 1740000 | 113880
6 | GE | Natural Gas | 823 | 8400 | 1900000 | 140160
7 | Caterpillar | Natural Gas | 1000 | 8865 | 1500000 | 150000
8 | GE | Natural Gas | 1029 | 10320 | 2085000 | 157680
Optimization | DECISION VARIABLES | Parameters |  |  |  |  | Constraints (SCFH)
Conditioner ID | Number of Units | Capital Cost | O&M Cost | Summed Cost | Gas Conditioning Cap. | Total Conditioning Capacity | 23700 | ≥ | 17986.9 | Total Conditionable Biogas
1 | 0 | 0 | 0 | 0 | 0 | Total Generator Gas Consumption Capacity | 11550 | ≥ | 10252.533 | Total Conditioned Biogas
2 | 0 | 0 | 0 | 0 | 0 | Decision Variables |  | = | Integers
3 | 1 | 1500000 | 1637993.4362 | 3137993.4362 | 23700 | Total Conditioning Cost
4 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 3137993.4362
Generator ID | Number of Units | Capital Cost | O&M Cost | Summed Cost | Gas Consumption Cap.
1 | 7 | 595000 | 1302949.3243 | 1897949.3243 | 11550
2 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | Total Generator Cost
8 | 0 | 0 | 0 | 0 | 0 | 1897949.3243
MINIMIZATION
TOTAL PROJECT COST
5035942.7605